DETECTION OF FERRORESONANCE PHENOMENON FOR WEST ANATOLIAN ELECTRIC POWER NETWORK IN TURKEY

ABSTRACT

Ferroresonance is an electrical phenomenon in nonlinear character, which frequently occurs in power systems containing saturable transformers, and single or more-phase switching on the lines for disjunction the loads. In this study, the ferroresonance phenomena are considered under the modeling of the West Anatolian Electric Power Network of 380 kV in Turkey. The ferroresonance event is carried out using the switching to remove the loads at the end of the lines. In this sense, two different cases are considered. Firstly, the switching is applied at 2nd second and the ferroresonance effects are observed between 2nd and 4th second of the voltage variations. As a result the ferroresonance and non-ferroresonance cases observed before the ferroresonance are compared with each other using the Fourier transform techniques. Hence, the properties of the ferroresonance event, which are defined between the 100 and 200 Hz, are presented in the frequency domain.

Keywords— Ferroresonance, West Anatolian Electric Power System, Power System Modeling, Spectral Analysis, Feature Extraction.

DETECÇÃO DE FENÔMENO ferrorressonância Oeste da Anatólia Energia Elétrica Sistema NA TURQUIA

RESUMO

Ferrorressonância é um fenômeno elétrico em caráter não-linear, o que freqüentemente ocorre em sistemas de potência contendo transformadores saturável, e um ou mais fases, ligar as linhas de separação das cargas. Neste estudo, os fenômenos ferrorressonância são considerados sob a modelagem da Anatólia ocidental Rede de Energia Elétrica de 380 kV, na Turquia. O evento ferrorressonância é realizada utilizando a mudança para remover as cargas, no final das linhas. Nesse sentido, dois casos são considerados diferentes. Em primeiro lugar, a mudança é aplicada em 2 segundos e os efeitos ferrorressonância são observados entre 2 e 4 do segundo variações de tensão. Como resultado, o ferrorressonância e casos ferrorressonância não observado antes do ferrorressonância são comparados uns com os outros usando a transformada de Fourier técnicas. Assim, as propriedades do evento ferrorressonância, que são definidos entre os 100 e 200 Hz, são apresentados no domínio da freqüência.

Palavras-chave- Ferrorressonância, Oeste da Anatólia Energia Elétrica Sistema, Energia Elétrica Sistema Modelagem, Análise Espectral, Exraction recurso.

- INTRODUCTION

At result studies, the related literature, the ferroresonance is defined as a general term applied to a wide variety of interactions between capacitors and iron-core inductors that result in unusual voltages and/or currents [1-11]. This term was first time used by P. Boucherot in 1920 to appellation of oscillations in circuits with nonlinear inductance and capacitance [12].  Nowadays, more suitable mathematical tools used for investigations the ferroresonance are provided through the nonlinear dynamic methods [11]. In this sense, the ferroresonance phenomenon is known as a nonlinear phenomenon that cause to overvoltage in power systems. Here, magnitudes of the over voltage variations are several times of the steady case amplitudes in time domain as well as some harmonics and other frequency components which are defined in the frequency domain. As a result, these high over-voltages cause to failures in transformers, cables, and arresters of the power system [1-12].  Also, in terms of the frequency components, the abnormal rates of harmonics can often be dangerously for most electrical equipment in the power systems. In this manner, frequency domain analysis of the ferroresonance phenomenon is very important to define its characteristic properties.

The effect of the ferroresonance can not be only described as the jump to a higher frequency state, but also it is given with bifurcations to the sub-harmonic, quasi-periodic, and chaotic oscillations in any circuit containing a nonlinear inductor [3, 11, 13]. This term was first time used by P. Boucherot in 1920 to appellation of oscillations in circuits with nonlinear inductance and capacitance [12]. A more suitable mathematical tool for studying ferroresonance and other nonlinear systems is provided by nonlinear dynamic methods [11].

In this research, the West Anatolian Electric Power Network of 380 kV in Turkey is considered for modeling and simulation of the ferroresonance event. The modeling and simulation studies are performed in the MATLAB-SIMULINK environments. Consequently, the ferroresonance event is carried out using the switching to remove the loads at the end of the lines.  Ferroresonance and non-ferroresonance parts of the voltage variations for single phase are compared with each other. Hence some frequency components, which are represented as features of the ferroresonance phenomenon, are determined between 100 and 200 Hz using the spectral analysis methods. Also, the role of the time delaying due to switching operation is emphasized with highly correlated results appeared at around 3rd, 5th, and 7th harmonics of the fundamental frequency.

- SPECTRAL ANALYSIS METHODS

Short time Fourier transform (STFT) is an alternative method to classical Fourier transform in terms of the non-stationary data analysis. In this manner, spectrogram approach based upon the STFT is used to track the non-stationary data on time-frequency plane. Under this section, Power Spectral Density variation, which is defined for stationary case, is introduced as well as the short Fourier transform technique. Besides, coherence analysis approach is defined to show the correlation between the signals in frequency domain. These spectral analysis methods are affectedly used in the various fields of the power engineering [14].

## 2.1. Power Spectral Density and Coherence Approach

A common approach for extracting the information about the frequency features of a random signal is to transform the signal to the frequency domain by computing the discrete Fourier transform. For a block of data of length N samples the transform at frequency mf is given by

X(mΔf)=k=0N−1x(kΔt) exp−j2πkmN.	(1)

Where f is the frequency resolution and t is the data-sampling interval. The auto-power spectral density (APSD) of x(t) is estimated as

Sxx(f)=1N X(mΔf)2,  f = mf.	(2)

The cross power spectral density (CPSD) between x(t) and y(t) is similarly estimated. The statistical accuracy of the estimate in Equation (2) increases as the number of data points or the number of blocks of data increases.

The cause and effect relationship between two signals or the commonality between them is generally estimated using the coherence function. The coherence function is given by

Cxy(f)=Sxy(f)Sxx(f)Syy(f), 0  Cxy  1 .	(3)

Where Sxx and Syy are the APSDs of x(t) and y(t), respectively, and Sxy is the CPSD between x(t) and y(t). A value of coherence close to unity indicates highly linear and close relationship between the two signals [15].

## Short Time Fourier Transform and Spectrogram

The short time Fourier transform (STFT) introduced by Gabor 1946 is useful in presenting the time localization of frequency components of signals. The STFT spectrum is obtained by windowing the signal through a fixed dimension window. The signal may be considered approximately stationary in this window. The window dimension fixed both time and frequency resolutions. To define the STFT, let us consider a signal x(t) with assumption that it is stationary when it is windowed through a fixed dimension window  g(t), centered at time location τ. The Fourier transform of the windowed signal yields the STFT [15].

STFTx(t)≡X(τ,f)=−∞+∞x(t)g(t−τ)exp[−j2πft]dt      	(4)

The equation maps the signal into a two-dimensional function in the time-frequency (t, f) plane. The analysis depends on the chosen window g(t). Once the window g(t) is chosen, the STFT resolution is fixed over the entire time-frequency plane. In discrete case, it becomes

STFTx(n)≡X(m,f)=n=−∞+∞x(n)g(n−m) e−jwn            	 (5)

The magnitude squared of the STFT yields the “spectrogram” of the function.

Spectrogramx(t)≡X(τ,f)2                                 	(6)

Using the spectrogram, non-stationary properties of the signal can be easily determined on the time-frequency plane.

- FERRORESONANCE PHENOMENA

Ferroresonance is a jump resonance, which can suddenly jump from one normal steady-state response (sinusoidal line frequency) to another ferroresonance steady-state response. It is characterized by overvoltage, which can cause to dielectric and thermal problems in transmission and distribution systems. Due to the nonlinearity of the saturable inductance, ferroresonance possesses many properties associated with a nonlinear system, such as:

- Ferroresonance is highly sensitive to the change of initial conditions and operating conditions.

- Ferroresonance may exhibit different modes of operation which are not experienced in linear system.

- The frequency of the voltage and current waveforms may be different from the sinusoidal voltage source.

- Ferroresonance possesses a jump resonance, whereas the voltage may jump to an abnormally high level.

- MODELING OF THE WEST ANATOLIAN ELECTRIC POWER SYSTEM

There are two aspects to be considered in this section. The first one is the modeling of the power system with MATLAB-SIMULINK TM  and the second one is related to the various simulations to be realized on this model to observe the behavior of the ferroresonance phenomena.

  - Modeling of the power system

Modeling of the West Anatolian Electric Power Network model of 380 kV in Turkey is represented as shown in figure1. The modeling and simulation studies are realized by using the MATLAB Power System Block-set.

Figure 1. Simplified Model of Oymapinar-Seydisehir line for West Anatolian Power Network in Turkey

The parameters of all electrical equipments used in the simplified model of the sample power system can be shown by the following table.

Table 1. Parameters of electrical components used in Oymapinar-Seydisehir line.

| Electrical Components | Parameters |
| --- | --- |
| Generator | 180 MVA, 14.4 kV, 50 Hz |
| Transformers | TR1:180 MVA, 14.4kV/ 380kV TR2: 600kVA, 380kV / 154kV TR3: 600kVA, 380kV / 154kV |
| Lines | π Line(B1-B2): 85.104 km R:0.2568 Ω/km L: 2 mH/km C: 8.6 nF/km Line(B2-B3): R:1Ω L:1mH |
| Loads | L1:P=50 MW, Qc=17 MVAR L2:P=112MW, QL=86 MVA |
| Switches | S1: 2 – 4 sec. on 0 - 2 sec. off S2: 2 – 4 sec. on 0 - 2 sec. off |

4.2. Simulations on the model

Using the simplified model as shown in Figure 1, ferroresonance phenomena are created under the scenarios which are given by table 2. In the table 2 switches (S1) and (S2) are used to remove the loads L1 and L2. Considering the various combinations of the switch states, voltage measurements are taken from Bus-2 and Bus-3 of the power system. Before the ferroresonance, all switches are on positions while the ferroresonance phenomena are occurred in different on-off positions of the switches. These different situations are indicated by cases 1-4 as given in the table 2.

Table 2. Different combinations of the switches.

Taking the case 1 which is denoted in the table 2, the voltage variations can be shown by the following figures for three phase measurements. As seen in Figure 2, the ferroresonance phenomenon begins at 2nd second and then, it causes to over- voltage as a result of the load removing.

Figure 2. Overall data for three phase measurements in Case 1

a) Phase-R, b) Phase-S, c) Phase-T

In this study, the phase R is used for the data analysis because the others are similar.  Data including the both parts of the ferroresonance and non-ferroresonance in case 1 is called as overall data.  Time - frequency variation of the overall data for the case 1 can be shown by Figure 3.

TIME-FREQUENCY ANALYSIS RESULTS AND FEATURE EXTRACTION

The time-frequency analysis of the voltage measurement for the phase R, in the case 1, is shown by the figure 3. Here the limits of the ferroresonance phenomenon are easily determined. According to these limitations, the most important features can be extracted from the frequency range, that defined between the 0 and 500 Hz, through the figure 3.

Figure 3. Characteristics of the voltage variation for the phase R in Time-Frequency plan.

Namely, huge amplitudes can be observed between 0 and 500 Hz as seen in the figure 3. For this reason the power spectral density (PSD) variation of this signal is presented between 0 -500 Hz. Hence, considering the PSD shown in Figure 4, fundamental frequency at 50 Hz and a small peak appeared at 100 Hz are determined the for overall data as well as small bifurcation effect seen of the fundamental frequency.

Figure 4. PSD for overall data in Case 1.

However, for more specific determination instead of the overall data, its non-ferroresonance and ferroresonance parts are considered respectively. Thus, PSD of the non-ferroresonance part is shown by means of figure 5. As seen in figure 5, there is a small peak at 150 Hz as well as the fundamental frequency at 50 Hz. However, increasing in the number of the bifurcation states occurred at 50 Hz is observed.

Figure 5.  PSD for non-ferroresonance part of the overall data.

In this sense, this situation can be interpreted as a result of the ferroresonance phenomenon and then, considering the ferroresonance part of the overall data Figure 6 shows these effects with other details.

Figure 6.  PSD for the ferroresonance part of the all data.

In terms of the comparisons of the ferroresonance and non ferroresonance parts of the overall data in spectral domain, which are shown by figure 7, the most important features of the ferroresonance phenomena are defined by the bifurcations of around the 50 Hz and the additional frequency components observed in the frequency range of 100-200 Hz, which has a central frequency at 150 Hz.  Similar results are obtained for the case2, 3 and 4 defined in Table 1. The effects of these cases can be detailed through the coherence analysis approach as indicated in section 5 and 6.

Figure 7.  Comparisons of the PSDs for partial and overall data.

- COHERENCE ANALYSIS

In the simplified model of the power system shown in figure 1, two switches (S1 and S2) are used to disjoint the loads from the system. The different combinations of operational modes of the switches can be shown by different cases as indicated in Table 1.  In these cases, switch-on and off positions can be arranged for same switching time or different switching time considering a specific time delay according to each others. Under these scenarios, the measurements are taken from the different buses (Bus 2 and 3) to show the ferroresonance effects. Hence, the coherence functions are based on the measurements taken from the Bus-2 and 3 for the cases 1, 2, 3 and 4 and the related results are interpreted through the figure 8. The coherence analysis results shown for case 1 and 3 give same results with each others. In this sense, the most different state is the case 4, which uses the time delay in switching. In the case 4, the time delay related to the switching cause to higher correlated results.

Figure 8. Coherences for all data in case 1, 2, 3 and 4.

In terms of the symbolic description of the coherence analysis, the coherence functions can be described by the functions Cij,k( f ):   i=1, 2, 3, 4 and    j, k=1, 2  for  j  k. Here subscripts j and k are bus numbers while the index i indicates the cases.

These functions shows the relationships between the measurement pairs taken from the Bus 2 and Bus 3 using as index the cases.  According to these measurement pairs, the high correlated results can be given for the case 4 as mentioned above. In the case 4, the time delay Δt is different from zero, namely switching time between S1 and S2 for the case 4 is positive and this time difference causes to the high correlation levels. For Δt=0 as defined in case 3 and case 1. The correlation functions reflect the same characteristics.

- CONCLUSIONS AND DISCUSSIONS

In this study, the ferroresonance phenomena are considered under the modeling of the West Anatolian Electric Power Network of 380 kV in Turkey. The ferroresonance event is carried out using the switching to remove the loads at the end of the lines. Ferroresonance and non-ferroresonance parts of the voltage variations for single phase are compared with each other using the power spectral density functions. In this sense, PSD results show that the fundamental properties of the ferroresonance phenomenon are localized between 100 and 200 Hz and it is observed a bifurcation at around the fundamental frequency 50 Hz. However, according to coherence analysis results, these frequency interval can be generalized between 0-200 Hz as well as the frequency region between 200 and 500 Hz. In the coherence approach, the most impressive results are related to the time delaying of the switching used to remove the loads. However, the second switch (S2) is on the line of load L2 (inductive), for this reason the effect of this load in switching duration will be stronger than the L1(capacitive).  In this manner this switching mode (S2) plays more dominant role over the S1. Also, if Δt 0 it will cause to high correlation levels, here the measure of the Δt is important, small Δt values cause to bigger effects with their impulsive characteristic. Therefore the effect of the case 4 is observed between the 0-500 Hz with high correlated frequency components. Roughly, the frequency values of these high correlation levels can be classified at 50, 150, 250 and 350 Hz. Hence these are also interpreted as 3rd, 5th and 7th harmonics of the fundamental frequency.

REFERENCES

- Kumar, G., Rajan, S., Rangarajan, R., Analysis of Ferroresonance in a Power Transformer with Multiple Nonlinearities, International Journal of Emerging Electric Power Systems, Volume:7, Issue:2, Article:2, (2006).

- Tanggawelu, B., Mukerjee, R.N., Ariffin, A.E., Ferroresonance Studies in Malaysian Utility’s Distribution Network, Proc. IEEE Power Engineering Society General Meeting, 2, 1216-1219 (2003).

- Stojkovsa, B., Stefanovska, A., Glob, R., Grgic, D., Time –Delay Feedback Control of Ferroresonant Chaotic Oscillations, IEEE Porto Power Tech Conference 10th-13th September, Porto Portugal, (2001).

- M.R. Iravani, Chair, Modeling and analysis guide- lines for slow transients- part III: the study of ferroresonance, IEEE Working Group on Modeling and Analysis of Systems Transients, IEEE Transactions on Power Delivery, 15, 255- 265 (2000).

- Saied M.M., Abdallah H.M. and Abdallah A.S., Damping Effect of Load on the Ferroresonance Phenomenon in Power Networks, Electric Power System Research, 7, 271-277 (1984).

- A.S. Abdallah and M.A. El-Kady., Ferroresonance Phenomenon in Power Transformers - Experimental Assessment, JKAU: Eng. Sci., vol. 16 no. 1, pp. 71-82 (2005 A.D./1426 A.H.)

- Buigues, B., Zamora, I., Valverde, V., Mazon, A.J., San Martin, J.I., Ferroresonance In Three –Phase Power Distribution Transformers: Sources, Consequences and Prevention,   19th International Conference on Electricity Distribution, paper:0197,CIRED,  Vienna 21-24 May. (2007).

- Charalambous, C., Wang, Z.D., Li, J., Osborne, M., Jarman, P., Validation of a Power Transformer Model for Ferroresonance with System Tests on a 400 kV Circuit, International Conference on Power Systems Transients (IPST’07), Lyon, France, 4-7 June, (2007).

- Jacobson D.A.N., Marti, L., Menzies, R.W., Modeling Ferroresonance in a 230 kV Transformer - Terminated Double - Circuit Transmission Line, Proc. of the 1999 International Conference on Power Systems Transients, Budapest, 451-456 (1999).

- Jacobson D.A.N., Menzies R. W., Investigation of Station Service Transformer Ferroresonance in Manitoba Hydro's 230-kV Dorsey Converter Station, Proc. IPST'2001, International Conference on Power Systems Transients, Rio de Janeiro (2001).

- Sakarung, P., “Application of PSCAD/EMTDC and Chaos Theory to Power System Ferroresonance Analysis”, International Conference on Power Systems Transients (IPST’05) in Montreal, Canada on June 19-23, 2005, Paper No. IPST05 – 227, (2005).

- Sutherland, P.E., Manning, R., “Ferroresonance in a 13.8kV Distribution Line”, IEEE page:2238-2241, (2006).

- Amir Tokic, A., Vlado Madzarevic, V., and Ivo Uglesic, I., “Numerical Calculations of Three-Phase Transformer Transients”, IEEE Transactions On Power Delivery, Vol.20, No:4, October, (2005).

- Taskin, S., Seker, S., Karahan, M., Akinci, T.C., “  Spectral Analysis for Current and Temperature Measurements in Power Cables”,  Electric Power Components and  Systems, Volume:37, Issue:4 , pages 415 – 426, April (2009).

- V.S. Vaseghi, Advanced signal processing and digital noise reduction, New York: John Wiley, (1996).